## Instructions
How to use this tool
Introduction: This tool is intended to be used in order to compare the costs of buying, running and servicing a water scheme with a diesel generator vs an equivalent stand alone solar pumping solution.
Costs are estimated for a period of 25 years (lifespan of solar panels, the longest of all components).
Costs that are common for both systems (e.g. salary of a guard for the water scheme) have been taken out, since they would have no impact in the cost comparision analysis.
Costs are calculated including pumping equipemnt (pump, genertor, solar panels, invertor and accessories). By adding additional columns, other costs could be included in the analysis if necessary.
Before proceeding to use the tool, read the Word document 'Technical Briefing - Ecoonomic Assessment', where principles of Net Present Value analysis are explained.
Tab 0: 'EXAMPLE'
An example of a real field case with costs for generator and hybrid system components is given an worked out through Tabs 3 to 5
Tab 1: 'Reference Costs for Generators'
Costs of Generators for Juba (South Sudan) are given on table on the left. Get prices of generators for your particular country/ location
Cost of Generator servicing is given on table on the right. Different servicing costs are given depending on the working hours of the generator and the quality of brand (high or low).
Thee prices are used in the cost calculation under tab 'Generator System'. Use these prices as a reference, unless you have a more accurate information on the costs for mainting a generator in your location.
Tab 2: 'Generator Fuel Consumption'
This table is a refernce for fuel consumption. Iedally your generator should be sized to work at 75% of its load and so you should use fuel consumption data from the 75% column.
If this is not the case or you have real data from the field, feel free to use the consumption you believe is closer to reality. This data will be used in tab 'Generator System'.
Tab 3: 'Generator System'
In this tab total costs for buying, operating, maintaing and replacing the generator will be estimated for a period of 25 years.
Fill only the cells in yellow.
Get discount factor for your country at http://data.worldbank.org/indicator/FR.INR.RINR?year_high_desc=false or in the Annex a of the Word document 'Technical Briefing - Economic Assessment'.
The cost of 1L of fuel should compromise costs to buy, store and transport fuel to the water scheme site.
Tab 4: 'Solar (Hybrid)'
In this tab total costs for buying, operating, maintaing and replacing the solar pumping part of the hybrid system will be estimated for a period of 25 years.
Fill only the cells in yellow.
Cost of Solar Pumping solution should include all costs involved to buy and install the solar system (including invertor).
Preventive and minor service (like cleaning and 1 or 2 visits of contractor technician to the field for preventive maintenance) is estimated at a flat rate of 1,500USD. Feel free to change I ncase rea ldata are avaible.
Tab 5: 'Generator (Hybrid)'
In this tab total costs for buying, operating, maintaing and replacing the generator pumping part of the hybrid system will be estimated for a period of 25 years.
Normally, the only difference with Tab 3 should be the annual working hours of the generator, that will be less than in Tab 3 since the solar part of the hybrid system will take over the generator during the solar day.
Fill only the cells in yellow.
Tab 6: 'Hybrid (Solar & Generator)'
In this Tab costs for solar and generator parts of the hybrid systems are add up.
Tab 7: 'Graph'
A comparative graph is automatically generated. Get the Return on Investment (point were both lines cross) and the costs saving (difference between the 2 lines after 25 years) as main information.

## 0 EXAMPLE
DIESEL GENERATOR STAND ALONE SYSTEM |  |  |  | EQUIVALENT HYBRID (SOLAR+GENERATOR) SYSTEM
Component | Unit | Qty | Total Price (USD) | Component | Unit | Qty | Unit Price | Total Price (USD)
Pump | Watt | 7500 | 4878.5714 | Pump | Watt | 7500 | 0.65048 | 4878.5714
Generator | kVA | 20 | 9500 | Inverter | Watt | 7500 | 0.27 | 2025
Electrical Connection Board | Unit | 1 | 1850 | Solar Modules | Watt | 14580 | 0.99206 | 14464.2857
Cables & Low level | m | 150 | 1400 | DC Accessories | Watt | 14580 | 0.16352 | 2384.1771
Transport | km | 1570 | 2700 | Cables & Low level | m | 150 | 11.7738 | 1766.0714
Installation | Day | 2 | 800 | Support Structure | Watt | 14580 | 0.2469 | 3599.8714
Total Price |  |  | 21128.5714 | Transport | km | 1570 | 2.28 | 3579.6
|  |  |  | Installation | Day | 14 | 400 | 5600
|  |  |  | Total Price |  |  |  | 38297.5771
Discount factor in country Uganda | 16%
Cost of 1 liter of diesel in USD: | 1.1 |  |  | Discount factor in country Uganda | 16%
Consumption of diesel (l/h) | 4.2
Running time of generator (hours/day): | 14 |  |  | Solar Pumping
Safe Yield (m3/h): | 20 |  |  | Running time of solar (hours/day): | 8h to 17h
Daily water provided (m3/d): | 280 |  |  | Safe Yield (m3/h): | 20
|  |  |  | Daily water provided with solar (m3/h): | 130
Generator Pumping
|  |  |  | Consumption of diesel (l/h) | 4.2
|  |  |  | Running time of generator (hours/day): | 7.5
|  |  |  | Daily water provided with generator (m3/h): | 150
|  |  |  | Total Daily water provided by Hybrid system (Solar + Generator) in m3/d: | 280

## 1 Reference Cost for Generators
Diesel Genset (Indicate Brand) |  | Prices (USD) | General Reference for Maintenance of Gensets
12.5 | kVA | 4500
15 | kVA | 6000 | Genset Maintenance | Good Quality Engine |  | Low Quality Engine
20 | kVA | 12000 | Maintenance and Replacement | Frequency of change (h) | Price (USD) | Frequency (hours) | Price (USD)
30 | kVA | 18500 | Minor Service | 250 | 20 | 250 | 20
45 | kVA | 22500 | Major Service | 1000 | 180 | 1000 | 125
60 | kVA | 30000 | Overhaul | 10000 | 30% of new | 5000 | 60% of new
80 | kVA | 34000 | Replacement | 35000 | See 'Cost of New Gensets' | 10000 | See 'Cost of New Gensets'
100 | kVA | 40000

## 2 Generator Fuel Consumption
Genset Fuel Consumption chart
Generator |  | Liter/hour
kVA | kW | Load 25% | Load 50% | Load 75% | Load 100%
25 | 20 | 2.3 | 3.4 | 4.9 | 6
38 | 30.4 | 4.2 | 6.8 | 9.1 | 11
50 | 40 | 6 | 8.7 | 12.1 | 15.1
75 | 60 | 6.8 | 11 | 14.4 | 18.1
94 | 75.2 | 9.1 | 12.9 | 17.4 | 23.1
125 | 100 | 9.8 | 15.5 | 21.9 | 28
156 | 124.8 | 11.7 | 18.9 | 26.8 | 34.4
169 | 135.2 | 12.5 | 20.4 | 28.7 | 37
188 | 150.4 | 13.6 | 22.3 | 31.8 | 41.2
219 | 175.2 | 15.5 | 25.7 | 36.7 | 48
250 | 200 | 17.1 | 29.1 | 41.6 | 54.4
288 | 230.4 | 20 | 33.3 | 47.3 | 62.7
313 | 250.4 | 21.6 | 35.9 | 51.4 | 68
375 | 300 | 25.7 | 42.7 | 60.9 | 81.3
438 | 350.4 | 29.9 | 49.5 | 70.7 | 94.9
500 | 400 | 33.6 | 56.3 | 80.5 | 108.1
625 | 500 | 41.6 | 69.9 | 99.8 | 134.9
750 | 600 | 49.9 | 83.2 | 119.1 | 161.8
938 | 750.4 | 61.6 | 103.6 | 148.6 | 201.9
1250 | 1000 | 81.6 | 137.6 | 196.9 | 268.8
1563 | 1250.4 | 101.7 | 171.2 | 245.7 | 335.7
1875 | 1500 | 121.7 | 205.3 | 294.1 | 402.6
2188 | 1750.4 | 141.8 | 238.9 | 342.8 | 469.5
2500 | 2000 | 161.8 | 272.9 | 391.5 | 536.4
2813 | 2250.4 | 181.8 | 306.6 | 440 | 603.3

## 3 Generator System
Real interest Rate/ Discount factor (d) | 0.12
Capital Cost of Generator (USD) | 9500
Cost of total Generator System (including capita cost of generator, transport, installation and others) | 21128.5714
Cost of 1 L of fuel (USD) | 1.1
Generator Running hours per day | 14
Year | Cost of total generator system | Generator Working time (hours/year) | Cumulative hours for overhaul | Cumulative hours for replacement | Minor Service | Major Service | Fuel Consumption (l/h) | Cost of fuel | Overhaul | Replacement | Pr Factor | Total Costs in Present Worth (USD)
n |  |  |  |  | 20 USD every 250h | 180 USD every 1000h |  |  | 30% genset cost every 10,000h | New genset every 35,000h | Pr = 1/(1+d)^n | PW = Cr*Pr
0 | 21128.5714 | 4956 | 4956 | 4956 | 396.48 | 892.08 | 4.2 | 22896.72 |  |  | 1 | 45313.8514
1 |  | 4956 | 9912 | 9912 | 396.48 | 892.08 |  | 22896.72 | 0 | 0 | 0.89286 | 21594
2 |  | 4956 | 4868 | 14868 | 396.48 | 892.08 |  | 22896.72 | 2850 | 0 | 0.79719 | 21552.3597
3 |  | 4956 | 9824 | 19824 | 396.48 | 892.08 |  | 22896.72 | 0 | 0 | 0.71178 | 17214.6046
4 |  | 4956 | 4780 | 24780 | 396.48 | 892.08 |  | 22896.72 | 2850 | 0 | 0.63552 | 17181.4092
5 |  | 4956 | 9736 | 29736 | 396.48 | 892.08 |  | 22896.72 | 0 | 0 | 0.56743 | 13723.3774
6 |  | 4956 | 4692 | 34692 | 396.48 | 892.08 |  | 22896.72 | 2850 | 0 | 0.50663 | 13696.9142
7 |  | 4956 | 4648 | 4648 | 396.48 | 892.08 |  | 22896.72 | 0 | 9500 | 0.45235 | 15237.51
8 |  | 4956 | 9604 | 9604 | 396.48 | 892.08 |  | 22896.72 | 0 | 0 | 0.40388 | 9768.029
9 |  | 4956 | 4560 | 14560 | 396.48 | 892.08 |  | 22896.72 | 2850 | 0 | 0.36061 | 9749.193
10 |  | 4956 | 9516 | 19516 | 396.48 | 892.08 |  | 22896.72 | 0 | 0 | 0.32197 | 7787.0129
11 |  | 4956 | 4472 | 24472 | 396.48 | 892.08 |  | 22896.72 | 2850 | 0 | 0.28748 | 7771.997
12 |  | 4956 | 9428 | 29428 | 396.48 | 892.08 |  | 22896.72 | 0 | 0 | 0.25668 | 6207.759
13 |  | 4956 | 4384 | 34384 | 396.48 | 892.08 |  | 22896.72 | 2850 | 0 | 0.22917 | 6195.7884
14 |  | 4956 | 4340 | 4340 | 396.48 | 892.08 |  | 22896.72 | 0 | 9500 | 0.20462 | 6892.6757
15 |  | 4956 | 9296 | 9296 | 396.48 | 892.08 |  | 22896.72 | 0 | 0 | 0.1827 | 4418.5602
16 |  | 4956 | 4252 | 14252 | 396.48 | 892.08 |  | 22896.72 | 2850 | 0 | 0.16312 | 4410.0398
17 |  | 4956 | 9208 | 19208 | 396.48 | 892.08 |  | 22896.72 | 0 | 0 | 0.14564 | 3522.4492
18 |  | 4956 | 4164 | 24164 | 396.48 | 892.08 |  | 22896.72 | 2850 | 0 | 0.13004 | 3515.6567
19 |  | 4956 | 9120 | 29120 | 396.48 | 892.08 |  | 22896.72 | 0 | 0 | 0.11611 | 2808.0749
20 |  | 4956 | 4076 | 34076 | 396.48 | 892.08 |  | 22896.72 | 2850 | 0 | 0.10367 | 2802.66
21 |  | 4956 | 4032 | 4032 | 396.48 | 892.08 |  | 22896.72 | 0 | 9500 | 0.09256 | 3117.8964
22 |  | 4956 | 8988 | 8988 | 396.48 | 892.08 |  | 22896.72 | 0 | 0 | 0.082643 | 1998.7323
23 |  | 4956 | 3944 | 13944 | 396.48 | 892.08 |  | 22896.72 | 2850 | 0 | 0.073788 | 1994.878
24 |  | 4956 | 8900 | 18900 | 396.48 | 892.08 |  | 22896.72 | 0 | 0 | 0.065882 | 1593.3771
[11 empty] | TOTAL COST | 250068.8061
Note on D18: Felipe Fischmann: If there was a replacement in a given year, reset the cumulative hour count to the sme count as the replacement count (for the new pump)
Note on E18: Felipe Fischmann: Starts from zero after 35000 hours

## 4 Solar (Hybrid)
Real interest Rate/ Discount factor (d) | 0.16
Cost of solar pumping solution (USD) | 38297.5771
Cost of Invertor (USD) | 2025
Year | Capital Cost | Preventive and Minor Service and | Major Service | Fuel Consumption (l/h) | Cost of fuel | Overhaul | Replacement of Invertor | Pr Factor | Total Costs in Present Worth (USD)
n |  | Cleaning | _ |  |  | _ | Every 7 years | Pr = 1/(1+d)^n | PW = Cr*Pr
0 | 38297.5771 | 1500 | 0 | 0 | 0 |  |  | 1 | 39797.5771
1 |  | 1500 | 0 |  | 0 |  |  | 0.86207 | 1293.1034
2 |  | 1500 | 0 |  | 0 |  |  | 0.74316 | 1114.7444
3 |  | 1500 | 0 |  | 0 |  |  | 0.64066 | 960.9865
4 |  | 1500 | 0 |  | 0 |  |  | 0.55229 | 828.4366
5 |  | 1500 | 0 |  | 0 |  |  | 0.47611 | 714.1695
6 |  | 1500 | 0 |  | 0 |  | 2025 | 0.41044 | 1446.8089
7 |  | 1500 | 0 |  | 0 |  |  | 0.35383 | 530.7443
8 |  | 1500 | 0 |  | 0 |  |  | 0.30503 | 457.5382
9 |  | 1500 | 0 |  | 0 |  |  | 0.26295 | 394.4295
10 |  | 1500 | 0 |  | 0 |  |  | 0.22668 | 340.0254
11 |  | 1500 | 0 |  | 0 |  |  | 0.19542 | 293.1253
12 |  | 1500 | 0 |  | 0 |  |  | 0.16846 | 252.6943
13 |  | 1500 | 0 |  | 0 |  | 2025 | 0.14523 | 511.9237
14 |  | 1500 | 0 |  | 0 |  |  | 0.1252 | 187.793
15 |  | 1500 | 0 |  | 0 |  |  | 0.10793 | 161.8905
16 |  | 1500 | 0 |  | 0 |  |  | 0.093041 | 139.5608
17 |  | 1500 | 0 |  | 0 |  |  | 0.080207 | 120.311
18 |  | 1500 | 0 |  | 0 |  |  | 0.069144 | 103.7164
19 |  | 1500 | 0 |  | 0 |  |  | 0.059607 | 89.4107
20 |  | 1500 | 0 |  | 0 |  |  | 0.051385 | 77.0782
21 |  | 1500 | 0 |  | 0 |  | 2025 | 0.044298 | 156.1498
22 |  | 1500 | 0 |  | 0 |  |  | 0.038188 | 57.2816
23 |  | 1500 | 0 |  | 0 |  |  | 0.03292 | 49.3807
24 |  | 1500 | 0 |  | 0 |  |  | 0.02838 | 42.5696
[8 empty] | TOTAL COST | 50121.4496

## 5 Generator (Hybrid)
Real interest rate / Discount factor (d) | 0.16
Capital Cost of Generator (USD) | 9500
Cost of total Generator System (including capita cost of generator, transport, installation and others) | 21128.5714
Cost of 1 L of fuel (USD) | 1.1
Generator Running hours per day | 7.5
Year | Cost of total generator system | Generator Working time (hours/year) | Cumulative hours for overhaul | Cumulative hours for replacement | Minor Service | Major Service | Fuel Consumption (l/h) | Cost of fuel | Overhaul | Replacement | Pr Factor | Total Costs in Present Worth (USD)
n |  |  |  |  | 20 USD every 250h | 180 USD every 1000h |  |  | 30% genset cost every 10,000h | New genset every 35,000h | Pr = 1/(1+d)^n | PW = Cr*Pr
0 | 21128.5714 | 2737.5 | 2737.5 | 2737.5 | 219 | 492.75 | 4.2 | 12647.25 |  |  | 1 | 34487.5714
1 |  | 2737.5 | 5475 | 5475 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.86207 | 11516.3793
2 |  | 2737.5 | 8212.5 | 8212.5 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.74316 | 9927.9132
3 |  | 2737.5 | 950 | 10950 | 219 | 492.75 |  | 12647.25 | 2850 | 0 | 0.64066 | 10384.4202
4 |  | 2737.5 | 3687.5 | 13687.5 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.55229 | 7378.0568
5 |  | 2737.5 | 6425 | 16425 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.47611 | 6360.3938
6 |  | 2737.5 | 9162.5 | 19162.5 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.41044 | 5483.0981
7 |  | 2737.5 | 1900 | 21900 | 219 | 492.75 |  | 12647.25 | 2850 | 0 | 0.35383 | 5735.2228
8 |  | 2737.5 | 4637.5 | 24637.5 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.30503 | 4074.8351
9 |  | 2737.5 | 7375 | 27375 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.26295 | 3512.7889
10 |  | 2737.5 | 112.5 | 30112.5 | 219 | 492.75 |  | 12647.25 | 2850 | 0 | 0.22668 | 3674.3145
11 |  | 2737.5 | 2850 | 32850 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.19542 | 2610.5744
12 |  | 2737.5 | 587.5 | 587.5 | 219 | 492.75 |  | 12647.25 | 0 | 9500 | 0.16846 | 3850.8922
13 |  | 2737.5 | 3325 | 3325 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.14523 | 1940.082
14 |  | 2737.5 | 6062.5 | 6062.5 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.1252 | 1672.4845
15 |  | 2737.5 | 8800 | 8800 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.10793 | 1441.797
16 |  | 2737.5 | 1537.5 | 11537.5 | 219 | 492.75 |  | 12647.25 | 2850 | 0 | 0.093041 | 1508.0939
17 |  | 2737.5 | 4275 | 14275 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.080207 | 1071.49
18 |  | 2737.5 | 7012.5 | 17012.5 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.069144 | 923.6983
19 |  | 2737.5 | 9750 | 19750 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.059607 | 796.2916
20 |  | 2737.5 | 2487.5 | 22487.5 | 219 | 492.75 |  | 12647.25 | 2850 | 0 | 0.051385 | 832.9069
21 |  | 2737.5 | 5225 | 25225 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.044298 | 591.7744
22 |  | 2737.5 | 7962.5 | 27962.5 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.038188 | 510.1503
23 |  | 2737.5 | 700 | 30700 | 219 | 492.75 |  | 12647.25 | 2850 | 0 | 0.03292 | 533.6082
24 |  | 2737.5 | 3437.5 | 33437.5 | 219 | 492.75 |  | 12647.25 | 0 | 0 | 0.02838 | 379.1248
[11 empty] | TOTAL COST | 121197.9626
Note on D18: Felipe Fischmann: If there was a replacement in a given year, reset the cumulative hour count to the sme count as the replacement count (for the new pump)
Note on E18: Felipe Fischmann: Starts from zero after 35000 hours

## 6 Hybrid (Solar & Generator)
Year | Hybrid (Solar + Generator) Present Worth (USD)
0 | 74285.1486
1 | 12809.4828
2 | 11042.6576
3 | 11345.4067
4 | 8206.4934
5 | 7074.5633
6 | 6929.907
7 | 6265.9671
8 | 4532.3733
9 | 3907.2183
10 | 4014.3399
11 | 2903.6997
12 | 4103.5864
13 | 2452.0057
14 | 1860.2775
15 | 1603.6875
16 | 1647.6547
17 | 1191.8011
18 | 1027.4147
19 | 885.7023
20 | 909.985
21 | 747.9242
22 | 567.432
23 | 582.9889
24 | 421.6944
Total Cost for Hybrid | 171319.4123

## 7 Graph
Cumulative Cost
Year | Generator | Hybrid (Solar+Generator)
0 (Capital costs) | 21128.5714 | 59426.1486
1 | 45313.8514 | 74285.1486
2 | 66907.8514 | 87094.6313
3 | 88460.2111 | 98137.2889
4 | 105674.8157 | 109482.6956
5 | 122856.2249 | 117689.189 | Costs saved with solar after 5 years: | 5167.0359
6 | 136579.6023 | 124763.7523
7 | 150276.5165 | 131693.6594 | Costs saved with solar after 10 years: | 38632.0303
8 | 165514.0265 | 137959.6265
9 | 175282.0554 | 142491.9998 | Costs saved with solar after 25 years: | 78749.3938
10 | 185031.2484 | 146399.2181
11 | 192818.2613 | 150413.558
12 | 200590.2583 | 153317.2577
13 | 206798.0173 | 157420.8442
14 | 212993.8057 | 159872.8499
15 | 219886.4814 | 161733.1274
16 | 224305.0416 | 163336.8149
17 | 228715.0814 | 164984.4697
18 | 232237.5306 | 166176.2707
19 | 235753.1873 | 167203.6854
20 | 238561.2622 | 168089.3877
21 | 241363.9222 | 168999.3728
22 | 244481.8187 | 169747.297
23 | 246480.5509 | 170314.729
24 | 248475.429 | 170897.7179
25 | 250068.8061 | 171319.4123